## Intro
United States Department of Agriculture - Forest Service
Sustainable New Construction and Major Renovation Buildings Assessment and Compliance Checklist
An explanation of buildings that must comply with this checklist is found in the latest version of the Forest Service Handbook 7309.11 - Buildings and
Related Facilities Handbook Chapter 70 - Sustainable Buildings. The Compliance Checklist directly represent the requirements for Sustainable New
Construction and Major Renovation.
This tool is a Microsoft Excel workbook with 3 worksheets listed below:
1) Introduction
2) The Compliance Checklist for New Construction and Major Renovation
3) The Guidance for Using the New Construction and Major Renovations Checklist
Required References:
1) ASHRAE Standard 189.1-2011 - Standard for the Design of High-Performance Green Buildings
2) ASHRAE Standard 189.1-2011 - Standard for the Design of High-Performance Green Buildings User's Manual
3) ASHRAE Standard 55-2010 - Thermal Environmental Conditions for Human Occupancy
4) ASHRAE Standard 62.1-2010 - Ventilation for Acceptable Indoor Air Quality
5) ASHRAE Standard 90.1-2010 - Energy Standard for Buildings Except Low-Rise Residential Buildings
Electronic access for ASHRAE Standards can be found at the following website:
http://subscriptions.techstreet.com/sessions/new
For access, please contact WO Technology & Engineering Support. http://www.fs.fed.us/eng/contacts.htm
There is no limit on the number of users but only 2 users can access the system simultaneously.

## NC-MR Checklist
USDA - FOREST SERVICE Sustainable Building Assessment and Compliance Tool |  |  |  | Meets SUSTAINABILITY Requirements (Yes, No, Not Applicable) | Explanation | Documents on File
Checklist for Sustainable New Construction and Major Renovations
For design and construction of new buildings and major renovation project >5,000 GSF
Checklist also serves as compliance assessment and verification form, to be completed post-construction.
Requirements |  | Name | Signature
|  | Title | Date
Location
Building CN ID#
Employ Integrated Design Principles | Integrated Design | Initiates and maintains an integrated project team in all stages of the project's planning and delivery.
Establishes performance goals for siting, energy, water, materials, and indoor environmental quality along with other comprehensive design goals and ensures incorporation of these goals throughout the design and lifecycle of the building.
Considers all stages of the building's lifecycle, including deconstruction.
| Commissioning | Employ commissioning practices tailored to the size and complexity of the building and its system components in order to verify performance of building components and systems and help ensure that design requirements are met. This should include:
An experienced commissioning provider,
Inclusion of commissioning requirements in construction documents,
A commissioning plan,
Verification of the installation and performance of systems to be commissioned, and
A commissioning report.
Optimize Energy Performance | Energy Efficiency | Establish a whole building performance target that takes into account the intended use, occupancy, operations, plug loads, other energy demands.
Use ENERGY STAR® and/or FEMP-designated Energy Efficient Products, where available.
Option 1: New Construction: Reduce the energy use by 30% compared to the baseline building performance rating per the American National Standards Institute (ANSI)/American Society of Heating, Refrigerating and Air-Conditioning Engineers, Inc., (ASHRAE)/Illuminating Engineering Society of North America (IESNA) Standard 90.1-2007, Energy Standard for Buildings Except Low-Rise Residential (10 CFR 433.4).
Option 2: Major Renovations: Reduce the energy use by 20% below pre-renovations 2003 baseline.
Laboratory spaces may use the Labs21 Laboratory Modeling Guidelines.
| On-Site Renewable Energy | Per the Energy Independence and Security Act (EISA) Section 523, meet at least 30% of the hot water demand through the installation of solar hot water heaters, when lifecycle cost effective.
Per Executive Orders and EPAct, implement renewable energy generation projects on agency property for agency use, when lifecycle cost effective .
| Measurement and Verification | Per the Energy Policy Act of 2005 (EPAct) Section 103 and EISA Section 434, install building level meters in new major construction and renovation projects to track and continuously optimize performance.
| Benchmarking | Compare actual performance data from the first year of operation with the energy design target, preferably by using ENERGY STAR® Portfolio Manager for building and space types covered by ENERGY STAR®. Verify that the building performance meets or exceeds the design target, or that actual energy use is within 10% of the design energy budget for all other building types. For other building and space types, use an equivalent benchmarking tool such as the Labs21 benchmarking tool for laboratory buildings.
| Building System Controls | Each Federal agency shall ensure that any large capital energy investment in an existing building that is not a major renovation but involves replacement of installed equipment (such as heating and cooling systems), or involves renovation, rehabilitation, expansion, or remodeling of existing space, employs the most energy efficient designs, systems, equipment, and controls that are life-cycle cost effective.
Protect and Conserve Water | Indoor Water | Employ strategies that in aggregate use a minimum of 20% less potable water than the indoor water use baseline calculated for the building, after meeting the EPAct 1992, Uniform Plumbing Codes 2006, and the International Plumbing Codes 2006 fixture performance requirements. Specify EPA’s WaterSense-labeled products or other water conserving products where available.
The installation of water meters to allow for the management of water use during occupancy.
| Outdoor Water | Use water efficient landscape and irrigation strategies, such as water reuse, recycling, and the use of harvested rainwater, to reduce outdoor potable water consumption by a minimum of 50% over that consumed by conventional means (plant species and plant densities). Specify EPA’s WaterSense-labeled products or other water conserving products where available.
Choose irrigation contractors who are certified through a WaterSense labeled program.
The installation of water meters for locations with significant outdoor water use.
| Storm Water | Employ design and construction strategies that reduce storm water runoff and discharges of polluted water offsite.
Per EISA Section 438, to the maximum extent technically feasible, maintain or restore the predevelopment hydrology of the site with regard to temperature, rate, volume, duration of flow using site planning, design, construction, and maintenance strategies.
| Process Water | Per the Energy Policy Act of 2005 Section 109, when potable water is used to improve a building’s energy efficiency, deploy lifecycle cost effective water conservation measures.
Enhance Indoor Environmental Quality | Thermal Comfort | Meet ASHRAE Standard 55-2004, Thermal Environmental Conditions for Human Occupancy.
| Ventilation | Meet ASHRAE Standard 62.1-2007, Ventilation for Acceptable Indoor Air Quality.
| Moisture Control | Establish and implement a moisture control strategy for controlling moisture flows and condensation to prevent building damage, minimize mold contamination, and reduce health risks related to moisture.
| Daylighting | Achieve minimum daylight factor of 2% (excluding all direct sunlight penetration) in 75% of all space occupied for critical visual tasks and provide appropriate glare control. Critical visual tasks include office spaces and classrooms. Other space types are encouraged but not mandatory.
Alternative 1 - Provide automatic dimming controls, or
Alternative 2 - Provide accessible manual lighting controls.
| Low-Emitting Materials | Use low emitting materials for building modifications, maintenance, and cleaning. In particular, specify materials and products with low pollutant emissions, including composite wood products, adhesives, sealants, interior paints and finishes, carpet systems, and furnishings.
| Protect Indoor Air Quality During Construction | Conduct a minimum 72-hour flush-out with maximum outdoor air consistent with achieving relative humidity no greater than 60% and a minimum internal temperature of 60F.
| Environmental Tobacco Smoke Control | Implement a policy and post signage indicating that: Prohibits smoking within the building, and
Prohibits smoking within 25 ft of all building entrances, operable windows, and building ventilation intakes during building occupancy.
| Acoustic | To address the control of exterior background nosie in building projects and interior background noise.
Reduce Environmental Impact of Materials | Recycled Content | Per Section 6002 of the Resource Conservation and Recovery Act (RCRA), for EPA-designated products, specify products meeting or exceeding EPA's recycled content recommendations. If EPA-designated products meet performance requirements and are available at a reasonable cost, a preference for purchasing them shall be included in all solicitations relevant to construction, operation, maintenance of or use in the building.
| Biobased Content | Per Section 9002 of the Farm Security and Rural Investment Act (FSRIA), for USDA-designated products, specify products with the highest content level per USDA's biobased content recommendations. If these designated products meet performance requirements and are available at a reasonable cost, a preference for purchasing them shall be included in all solicitations relevant to construction, operation, maintenance of or use in the building.
For other products, specify biobased products made from rapidly renewable resources where products meet performance requirements and are available at a reasonbale cost.
For other products, specify biobased products made from certified sustainable wood products meet performance requirements and are available at a reasonbale cost.
| Environmentally Preferable Products | Use products that have a lesser or reduced effect on human health and the environment over their lifecycle when compared to competing products or services that serve the same purpose.
| Waste and Materials Management | Provide salvage, reuse and recycling services for the entire building. There shall be an area that is dedicated for the service and shall provide collection and storage materials for recycling.
During Construction: Divert a minimum of 50% of construction and demolition debris from disposal in landfills and incinerators by recycling and/or reuse.
| Ozone Depleting Compounds | Eliminate the use of ozone depleting compounds during and after construction where alternative environmentally preferable products are available, consistent with either the Montreal Protocol and Title VI of the Clean Air Act Amendments of 1990, or equivalent overall air quality benefits that take into account lifecycle impacts.
Other | Siting | Design, construct, maintain, and operate high performance sustainable buildings in sustainable locations. (Applies for buildings >=$2.5 million and is adjusted annually for inflation based on 2007)
| Greenhouse Gas | Reduce fossil fuel-generated energy consumption (compared to a similar building in fiscal year 2003): -55% beginning in FY 2010 -65% beginning in FY 2015 -80% beginning FY 2020 -90% beginning FY 2025 -100% beginning FY 2030 as measured by Commercial Buildings Energy Consumption Survey (CBECS) data. (Applies for buildings >=$2.5 million and is adjusted annually for inflation based on 2007)

## NC-MR Guidance
USDA - FOREST SERVICE Sustainable Building Assessment and Compliance Tool
Checklist for Sustainable New Construction and Major Renovations
| Federal Requirement | Source of Requirement | Performance Requirement | Recommended Method of Compliance |  | Suggested Documentation of Compliance
Employ Integrated Design Principles | Integrated Design | Guiding Principle | Initiates and maintains an integrated project team in all stages of the project's planning and delivery. | -Incorporate integrated design as described in ASHRAE 189.1 Informative Appendix H - Integrated Design | Integrated Design Process by Whole Building Design Guide: http://www.wbdg.org/resources/charrettes.php?r=engage_process | Design Charrette documents
Establishes performance goals for siting, energy, water, materials, and indoor environmental quality along with other comprehensive design goals and ensures incorporation of these goals throughout the design and lifecycle of the building.
Considers all stages of the building's lifecycle, including deconstruction.
| Commissioning | Guiding Principle, EISA Section 432 | Employ commissioning practices tailored to the size and complexity of the building and its system components in order to verify performance of building components and systems and help ensure that design requirements are met. This should include: | -Meet ASHRAE 189.1 Section 10.3.1.2 - Building Project Commissioning -Project shall include the following documents as required by commissioning practices: -Owner's project requirements -Commissioning requirements -Commissioning plan -Commissioning report -The sample project provided in the 'Sample Tool / Reference' column meets the intent of the Guiding Principle. | http://fsweb.wo.fs.fed.us/eng/programs/facilities/commissi.htm
|  |  | An experienced commissioning provider. |  |  | Commissioning Report
|  |  | Inclusion of commissioning requirements in construction documents. |  |  | Owner's project requirements and commissioning requirements
|  |  | A commissioning plan, |  |  | Commissioning Plan
|  |  | Verification of the installation and performance of systems to be commissioned. |  |  | Commissioning Report
|  |  | A commissioning report. |  |  | Commissioning Report
Optimize Energy Performance | Energy Efficiency1 | Guiding Principle, EPAct, EO 13423, EISA Section 431, 433, 524, 10 CFR 433 and 434 | Establish a whole building performance target that takes into account the intended use, occupancy, operations, plug loads, other energy demands. | Use Energy Star's Target Finder when following ASHRAE 189.1 Section 7.4 - Prescriptive Option. (Can be omited if using ASHRAE 90.1 - Normative Appendix G Performance Rating Method under the reduction in energy use Guiding Principle below) | https://www.energystar.gov/index.cfm?fuseaction=target_finder. | Energy Star's Target Finder results
|  |  | Use ENERGY STAR® and/or FEMP-designated Energy Efficient Products, where available. | Use ENERGY STAR® and FEMP-designated Energy Efficient Products (or products that meet or exceed these efficiency standards) where available and in all covered product categories. | Energy Star Product Specifications: http://www.energystar.gov/index.cfm?c=product_specs.pt_product_specs FEMP Product Specifications: https://www1.eere.energy.gov/femp/technologies/eep_purchasingspecs.html | Specifications
|  |  | -Option 1: New Construction: Reduce the energy use by 30% compared to the baseline building performance rating per the American National Standards Institute (ANSI)/American Society of Heating, Refrigerating and Air-Conditioning Engineers, Inc., (ASHRAE)/Illuminating Engineering Society of North America (IESNA) Standard 90.1-2007, Energy Standard for Buildings Except Low-Rise Residential (10 CFR 433.4). OR -Option 2: Major Renovations: Reduce the energy use by 20% below pre-renovations 2003 or more recent baseline. | -Meet ASHRAE 189.1 Section 7.4 - Prescriptive Option OR -ASHRAE 90.1 - Normative Appendix G Performance Rating Method • Energy consumption for the purposes of calculating the 30 percent savings shall include space heating, space cooling, ventilation, service water heating, lighting and all other energy consuming systems normally specified as part of the building design except for receptacle and process loads. | -Using ASHRAE 90.1 method: Requirements for the Performance Rating Method can be found in ASHRAE 90.1 Appendix G. Energy modeling must be used to show reduction in energy use and baseline building design in accordance with 10 CFR 434 sections 507 and 508. In accordance with 10 CFR 433.4, "if a 30% reduction is not life-cycle cost-effective, the design of the proposed building shall be modified so as to achieve an energy consumption level at or better than the maximum level of energy efficiency that is lifecycle cost-effective, but at a minimum complies with ASHRAE 90.1." Green Products Compilation: http://www.sftool.gov/greenprocurement | Design documents and/or energy models
|  |  | Laboratory spaces may use the Labs21 Laboratory Modeling Guidelines where the buildings predominantly lab spaces. | Meet Labs21 Modeling Guidelines |  | Design documents
| On-Site Renewable Energy | Guiding Principle, EO 13423, EISA Section 523 | Per the Energy Independence and Security Act (EISA) Section 523, meet at least 30% of the hot water demand through the installation of solar hot water heaters, when lifecycle cost effective. | 30% of the hot water demand met through the installation of solar hot water heaters, when lifecycle cost effective. | To determine cost/savings, use FEMP's calculator: http://apps1.eere.energy.gov/femp/solar_hotwater_system/index.cfm | Design documents or LCC calculations
|  |  | Per Executive Orders and EPAct, implement renewable energy generation projects on agency property for agency use, when lifecycle cost effective . | Implement renewable energy generation projects on agency property for agency use, when lifecycle cost effective. -EISA 2007 changed the life-cycle cost methodology for Federal buildings from 25 years to 40 years, which expands the number of potential cost-effective measures. -The following renewable energy resources are covered: solar, wind, geothermal, biomass, landfill gas, municipal solid waste, hydropower, ocean, and thermal energy. | For more detail on resources covered: http://www1.eere.energy.gov/femp/technologies/renewable_technologies.html | Design documents, renewable energy certificates or LCC calculations
| Measurement and Verification | Guiding Principle, EPAct, EISA Section 434 | Per the Energy Policy Act of 2005 (EPAct) Section 103 and EISA Section 434, install building level meters in new major construction and renovation projects to track and continuously optimize performance. | -At a minimum, meters are to be installed on all new buildings when life cycle cost effective. | -ASHRAE 189.1 Section 7.3.3 – Energy Consumption Management -FEMP Metering Best Practices Guide available at http://www1.eere.energy.gov/femp/pdfs/mbpg.pdf | Specifications and/or design documents
-Provide an advanced meter for each energy supply source to the building that exceeds for any of the the thresholds listed. -Electrical service: > 200 kVA -Gas and district services: > 1,000,000 Btu/h (300 kW) -Geothermal energy: > 1,000,000 Btu/h (300 kW heating)
-For buildings that exceed the threshold for advanced metering above AND exceed the thresholds below for each subsystem, provide a submeter for each subsystem to the building. -HVAC System: Connected electric load > 100 kVA -HVAC System: Connected gas or district services load > 500,000 Btu/h (150 kW) -People moving: Sum of all feeders > 50 kVA -Lighting: Connected laod > 50 kVA -Process and plug process: Connected load > 50 kVA -Process and plug process: Connected gas or district services load > 250,000 Btu/h (75 kW) -When it is cost effective, install submeters on renewable energy systems based on the following thresholds: -On-site renewable electric power: All systems > 1 kVA (peak) -On-site renewable thermal energy: > 100,000 Btu/h (30 kW)
| Benchmarking | Guiding Principle | Compare actual performance data from the first year of operation with the energy design target, preferably by using ENERGY STAR® Portfolio Manager for building and space types covered by ENERGY STAR®. Verify that the building performance meets or exceeds the design target, or that actual energy use is within 10% of the design energy budget for all other building types. For other building and space types, use an equivalent benchmarking tool such as the Labs21 benchmarking tool for laboratory buildings. | 1 YEAR POST OCCUPANCY -Input actual performance data from the first year of operation into Energy Star Portfolio Manager. -If the Prescriptive Option was used under the Energy Efficiency Guiding Principle, verify that the actual energy use meets or exceeds the design target (found from Energy Star Target Finder or equivalent). -If the Performance Rating Method was used under the Energy Efficiency Guiding Principle, verify that the actual energy use meets or exceeds the Proposed Building energy model. If actual performance is not within 10% of the design target/energy model, verify that the buidling's O&M is meeting the design intent. If the O&M is meeting the design intent but actual performance is not within 10% of the design target, make note and file in project folder. (Ex. Hotter summer than design, colder winter than design, plug loads may have been underestimated, etc.) | Energy Star Portfolio Manager: http://www.energystar.gov/index.cfm?c=evaluate_performance.bus_portfoliomanager | Energy Start Portfolio Manager results
| Building System Controls | EISA Section 434 | Each Federal agency shall ensure that any large capital energy investment in an existing building that is not a major renovation but involves replacement of installed equipment (such as heating and cooling systems), or involves renovation, rehabilitation, expansion, or remodeling of existing space, employs the most energy efficient designs, systems, equipment, and controls that are life-cycle cost effective. | Employ building system controls that are life-cycle cost effective. Controls may include but are not limited to the following: -Occupancy (Example: Smart Plug Strip) -Lighting (Example: Occupancy Sensor, Daylight Sensor, Dimming) -HVAC (Example: Programmable Thermostat, DDC) |  | Specifications and/or design documents
Protect and Conserve Water | Indoor Water*/Water-Efficient Products1 | Guiding Principle, EPAct, EO 13423, EO 13514, EISA Section 432 | -Employ strategies that in aggregate use a minimum of 20 percent less potable water than the indoor water use baseline calculated for the project, after meeting the EPAct 1992, Uniform Plumbing Codes 2006, and the International Plumbing Codes 2006 fixture performance requirements. -Specify EPA’s WaterSense-labeled products or other water conserving products where available. | Meet ASHRAE 189.1 Section 6.3.2 - Building Water Use Reduction. Use this section for fixture and equipment water use requirements. -NOTE: -Some plumbing fixtures may not be WaterSense-labeled, even though they meet the requirements of 20% less than EPAct. These fixtures will meet the intent of this Guiding Principle. | Zurn Watercalculator or equivalent: http://watercalculator.zurn.com/ Green Products Compilation: http://www.sftool.gov/greenprocurement | Calculation results
|  |  | Installation of water meters to allow for the management of water use during occupancy. | -At a minimum, meters are to be installed on all supply water sources including non-potable, alternative on-site water sources, and FS owned water systems when life cycle cost effective.
|  |  |  | -If the following water consumption rate applies, refer to ASHRAE 189.1 Section 6.3.3 - Water Consumption Measurement for advanced water metering requirements. -Potable or Municipally reclaimed water use > 1,000 gallons/day -Alternate sources of water use > 500 gallons/day | Zurn Watercalculator or equivalent: http://watercalculator.zurn.com/ | Calculation results
| Outdoor Water/Water-Efficient Products1 | Guiding Principle, EO 13423, EO 13514, EISA Section 432 | -Reduce outdoor potable water consumption by a minimum of 50 percent over that consumed by conventional means. -Specify EPA’s WaterSense-labeled products or other water conserving products where available. | -Meet ASHRAE 189.1 Section 6.3.1 - Site Water Use Reduction AND either -ASHRAE 189.1 - Section 6.4.1 - Prescriptive Option: Site Water Use Reduction OR -Section 6.5.1 - Performance Option: Site Water Use Reduction. | See ASHRAE 189.1 User's Manual Page 6-14 for example on calculating ET. Green Products Compilation: http://www.sftool.gov/greenprocurement | Calculation results
|  |  | Choose irrigation contractors who are certified through a WaterSense labeled program. | Choose irrigation contractors who are certified through a WaterSense labeled program. | http://www.epa.gov/watersense/meet_our_partners.html | Document partner name
|  |  | The installation of water meters for locations with significant outdoor water use. | Sub-metering of specific applications should be installed where cost-effective. Refer to ASHRAE 189.1 Table 6.3.3B Subsystem Water Measurement Thresholds for sub-metering requirements. Total Irrigated landscape area with controllers >25,000 ft2 Separate campus or project buildings consumption >1000 gal/day |  | Calculation results
| Storm Water | Guiding Principle, EO 13514, EISA Section 438 | Employ design and construction strategies that reduce storm water runoff and discharges of polluted water offsite. | -Meet ASHRAE 189.1 Section 5.4.1 - Prescriptive Option: Site Development OR -ASHRAE 189.1 - Section 5.5.1 - Performance Option: Site Development | ASHRAE 189.1 User's Manual Section 5.4.1 OR Section 5.5.1 | Design documents, calculation results, storm water pollution prevention plan
To the maximum extent technically feasible, maintain or restore the predevelopment hydrology of the site with regard to temperature, rate, volume, and duration of flow using site planning, design, construction, and maintenance strategies.
| Process Water | Guiding Principle, Epact | Per the Energy Policy Act of 2005 Section 109, when potable water is used to improve a building’s energy efficiency, deploy lifecycle cost effective water conservation measures. | If the building includes any of the following, refer to ASHRAE 189.1 Section 6.3.2.3 - HVAC Systems and/or Equipment and Section 6.4.2.1 - Cooling Towers for requirements. -Once-through cooling with potable water -Cooling towers or evaporative coolers -Consider condensate collection if life-cycle cost effective. Potential uses include but not limited to cooling tower make-up and irrigation. |  | Design documents
Enhance Indoor Environmental Quality | Thermal Comfort | Guiding Principle | Meet ASHRAE Standard 55, Thermal Environmental Conditions for Human Occupancy. | -Design to comply with ASHRAE Standard 55 Section 6.1 - Design AND Section 6.2 - Documentation | -Air Diffusion Performance Index (ADPI) is the best way of assuring that a space will meet ASHRAE 55. To calculate ADPI of a space, the measurement of temperature and velocities are required. Per ASHRAE, ADPI >=80 is acceptable. The software, TEAMS GRD made by TITUS calculates ADPI. http://www.titus-hvac.com/main/software2/index.aspx?prod=teams5download (Sample ADPI calculation/instructions have been placed on the O drive) -For sample thermal comfort document, refer to the O drive: O:\NFS\R08\NFS\Program\7100Engineering\FSH 7309.11 - Chapter 70 Reference Files\Thermal Comfort | Design documents
| Ventilation | Guiding Principle | Meet ASHRAE Standard 62.1, Ventilation for Acceptable Indoor Air Quality. | Designs and construction to comply with ASHRAE Standard 62.1 Section 4 through 7. | Recommend using ASHRAE software (Todd to send info) | Design documents
| Moisture Control | Guiding Principle | Establish and implement a moisture control strategy for controlling moisture flows and condensation to prevent building damage, minimize mold contamination, and reduce health risks related to moisture. | -Meet ASHRAE 189.1 Section 7.4.2.9 - Continuous Air Barrier AND -ASHRAE 189.1 - Section 10.3.1.5 - Moisture Control | For Continuous Air Barrier characteristics, see: ASHRAE 189.1 Normative Appendix B | Design documents
| Daylighting | Guiding Principle | Achieve minimum daylight factor of 2% (excluding all direct sunlight penetration) in 75% of all space occupied for critical visual tasks and provide appropriate glare control. Critical visual tasks include office spaces and classrooms. Other space types are encouraged but not mandatory. | -Meet ASHRAE 189.1 Section 8.4.1 - Prescriptive Option - Daylighting by Sidelighting OR -ASHRAE 189.1 - Section 8.5.1 - Performance Option - Daylighting Simulation | -Sidelighting Effective Aperture equation can be found in ASHRAE 189.1 User's Manual Section 8.4.1.1. Also see sample calculation in O drive: O:\NFS\R08\NFS\Program\7100Engineering\FSH 7309.11 - Chapter 70 Reference Files\Sidelighting -Additional information for calculating Primary Sidelighted Area on ASHRAE 189.1 under the Definitions section for 'Daylight Area' -ASHRAE 189.1 User's Manual Section 8.4.1 OR Section 8.5.1 | Calculation or Simulation results
|  |  | Alternative 1 - Provide automatic dimming controls, OR Alternative 2 - Provide accessible manual lighting controls. | -Alternative 1 - Provide automatic dimming controls Refer to ASHRAE 90.1 Section 9.4.1.4 - Automatic Daylighting Controls for Primary Sidelighted Areas and Section 9.4.1.5 - Automatic Daylighting Controls for Toplighting OR -Alternative 2 - Provide accessible manual lighting controls. |  | Design documents
| Low Emitting Materials | Guiding Principle, EO 13514 | Specify materials and products with low pollutant emissions including the following: Adhesives, sealants, paints and coatings, flooring systems, composite wood, and agrifiber products. | -Meet ASHRAE 189.1 Section 8.4.2 - Prescription Option: Materials OR -ASHRAE 189.1 - Section 8.5.2 - Performance Option: Materials -NOTE: All materials and products used on the interior of the building (inside of the weatherproofing system and applied on-site) must meet requirement. |  | Specifications, purchasing policy
| Protect Indoor Air Quality during Construction | Guiding Principle | Conduct a minimum 72-hour flush-out with maximum outdoor air consistent with achieving relative humidity no greater than 60% and a minimum internal temperature of 60F. | -Meet flush-out procedures in ASHRAE 189.1 Section 10.3.1.4 - Indoor Air Quality Construction Management OR -After construction and prior to occupancy, conduct a minimum 72-hour flush-out with maximum outdoor air consistent with achieving relative humidity no greater than 60% and a minimum internal temperature of 60F. |  | Specifications and log of flush-out
| Environmental Tobacco Smoke Control | Guiding Principle | Implement a policy and post signage indicating that: Prohibits smoking within the building. | Implement a policy and post signage indicating that: Prohibits smoking within the building. |  | Copy of policy and photo of signage
|  |  | Prohibits smoking within 25 ft of all building entrances, operable windows, and building ventilation intakes during building occupancy. | Prohibits smoking within 25 ft of all building entrances, operable windows, and building ventilation intakes during building occupancy. |  | Copy of policy
| Acoustic | EISA Section 433, 436 | To address the control of exterior background nosie in building projects and interior background noise. | -Meet ASHRAE 189.1 Section 8.3.3 - Acoustical Control -Omit Part C in Section 8.3.3.1 - Exterior Sound: 'Where yearly average day-night average sound levels at the property line exceed 65 decibels.' |  | Specifications
Reduce Environmental Impact of Materials | Recycled Content1 | Guiding Principle, Resource Conservation and Recovery Act, EO 13514 | Per Section 6002 of the Resource Conservation and Recovery Act (RCRA), for EPA-designated products, specify products meeting or exceeding EPA's recycled content recommendations. If EPA-designated products meet performance requirements and are available at a reasonable cost, a preference for purchasing them shall be included in all solicitations relevant to construction, operation, maintenance of or use in the building. | Purchase and/or specify EPA-designated products that meet or exceed EPA's recycled content recommendations. EPA's list of designated products include the following categories: - Construction Products - Landscaping Products - Nonpaper Office Products - Paper and Paper Products - Park and Recreation Products - Transportation Products - Vehicular Products - Miscellaneous Products -Specific products in each of the 8 categories can be found on the website provided in the 'Sample Tool / Reference' column. | Product Categories and recycled content recommendations: http://www.epa.gov/epawaste/conserve/tools/cpg/products/index.htm#construct Green Products Compilation: http://www.sftool.gov/greenprocurement | Specifications and/or requisitions that comply with purchase requirement, purchasing policy
| Biobased Content1 | Guiding Principle, Farm Security and Rural Investment Act, EO 13514 | Per Section 9002 of the Farm Security and Rural Investment Act (FSRIA), for USDA-designated products, specify products with the highest content level per USDA's biobased content recommendations. If these designated products meet performance requirements and are available at a reasonable cost, a preference for purchasing them shall be included in all solicitations relevant to construction, operation, maintenance of or use in the building. | Purchase and/or specify USDA-designated products that meet or exceed USDA's biobased content recommendations. | USDA-designated Product Categories and biobased content recommendations: http://www.biopreferred.gov/ProductCategories.aspx Green Products Compilation: http://www.sftool.gov/greenprocurement | Specifications and/or requisitions that comply with purchase requirement, purchasing policy
|  |  | For other products, specify biobased products made from rapidly renewable resources where products meet performance requirements and are available at a reasonbale cost. | Specify biobased products made from rapidly renewable resources where products meet performance requirements and are available at a reasonbale cost. | Green Products Compilation: http://www.sftool.gov/greenprocurement | Specifications and/or requisitions that comply with purchase requirement, purchasing policy
|  |  | For other products, specify biobased products made from domestically harvested wood products, ideally locally sourced and from National Forest System lands that meet performance requirements and are available at a reasonbale cost. | Specify biobased products made from certified sustainable wood products meet performance requirements and are available at a reasonbale cost. | Green Products Compilation: http://www.sftool.gov/greenprocurement | Specifications and/or requisitions that comply with purchase requirement.
| Environmentally Preferred Products1 | Guiding Principle, EO 13514 | Use products that have a lesser or reduced effect on human health and the environment over their lifecycle when compared to competing products or services that serve the same purpose. | Use products from the Green Products Compilation (link provided in Sample Tool / Reference) or equivalent. A number of standards and ecolabels are also available in the marketplace to assist specifiers in making environmentally perferable decisions. | Summary for Green Products Compilation: http://www.gsa.gov/portal/content/198257 Green Products Compilation: http://www.sftool.gov/greenprocurement | Specifications and/or requisitions that comply with purchase requirement, purchasing policy
| Waste and Materials Management | Guiding Principle, EO 13514 | Provide salvage, reuse and recycling services for the entire building. There shall be an area that is dedicated for the service and shall provide collection and storage materials for recycling. | Minimum recommended recycling room area (GSF) based on building (GSF): - 82 GSF for buildings 0-5,000 GSF - 125 GSF for buildings 5,001-15,000 GSF - 175 GSF for buildings 15,001-50,000 GSF - 225 GSF for buildings 50,001-100,000 GSF - 275 GSF for buildings 10,001-200,000 GSF - 500GSF for buildings >=200,001 GSF |  | Design documents
|  |  |  | Storage materials for recycling must include at a minimum: - Paper - Corrugated Cardboard - Glass - Plastics - Metals - Fluorescent and HID Lamps and Ballasts |  | Specifications
|  |  | During Construction: Divert a minimum of 50% (calculation can be done by weight or volume, but must be consistent throughout) of construction and demolition debris from disposal in landfills and incinerators by recycling and/or reuse. | -Meet ASHRAE 189.1 Section 9.3.1.1 - Diversion |  | Specifications
| Ozone Depleting Compounds1 | Guiding Principle, Montreal Protocol and Title VI of the Clean Air Act Amendments of 1990 | Eliminate the use of ozone depleting compounds during and after construction where alternative environmentally preferable products are available, consistent with either the Montreal Protocol and Title VI of the Clean Air Act Amendments of 1990, or equivalent overall air quality benefits that take into account lifecycle impacts. | Refrigerants in HVAC&R systems shall not be CFC-based. |  | Specifications, purchasing policy
|  |  |  | CFCs, HCFCs, and Halons shall not be used in fire suppression systems. |  | Specifications, purchasing policy
Other | Siting2 | EISA Section 433, EO 13514 | Design, construct, maintain, and operate high performance sustainable buildings in sustainable locations. (Applies for buildings >=$2.5 million and is adjusted annually for inflation based on 2007) | -Meet ASHRAE 189.1 Section 5.3 - Mandatory Provisions | ASHRAE 189.1 User's Manual Section 5.3 | Design documents
| Greenhouse Gas2 | EISA Section 433 | Reduce fossil fuel-generated energy consumption (compared to a similar building in fiscal year 2003): -55% beginning in FY 2010 -65% beginning in FY 2015 -80% beginning FY 2020 -90% beginning FY 2025 -100% beginning FY 2030 as measured by Commercial Buildings Energy Consumption Survey (CBECS) data. (Applies for buildings >=$2.5 million and is adjusted annually for inflation based on 2007) | EISA 2007 requires DOE to establish revised performance standards for the construction of all new Federal buildings, including commercial buildings, multi-family high-rise residential buildings and low-rise residential buildings. The provisions in the DOE’s Notice of Proposed Rulemaking (NOPR), published in the Federal Register, Vol. 75, No. 199 Friday, October 15, 2010 [Docket No. EERE–2010–BT–STD–0031], specifically address the reduction of fossil fuel-generated energy consumption in new Federal buildings and Federal buildings undergoing major renovations. In accordance with this NOPR, generated energy consumption reductions do not apply to Federal agencies until the regulations implementing the reductions are finalized in a FINAL RULE.
1. Per EO 13514 Section 2(h), Federal agencies are to ensure that 95% of new contract actions be sustainable acquisitions where such products and services meet agency performance requirements. Sustainable acquisition is defined as the purchasing and use of the following products:
A) | Recycled content
B) | Energy efficient (Energy Star labeled, FEMP-designated, and low standby power)
C) | Biobased content
D) | Environmentally preferable
E) | Water efficient
F) | Non-Ozone depleting
G) | Non-toxic or less toxic than their alternatives
Refer to "USDA Sustainable Procurement Program" located at 'O:\NFS\R08\NFS\Program\7100Engineering\FSH 7309.11 - Chapter 70 Reference Files' for more information.
2. $2.5 million cost includes design, permitting, construction (materials and labor), and commissioning costs. (Land and legal cost would generally not be included) (10 CFR Parts 433 and 435)
For sample commissioning documents: