section 13100

- lightning protection

part 1 – general

## summary

#### This Section includes lightning protection for a rappel training tower and simulator.

## submittals

#### Product Data:  For air terminals and mounting accessories indicated.

#### Shop Drawings:  Detail lightning protection system, including air-terminal locations, conductor routing and connections, and bonding and grounding provisions.  Include indications for use of raceway and data on how concealment requirements will be met.

#### Qualification data.

#### Field quality-control inspection reports.

## quality assurance

#### Installer Qualifications:  Engage an experienced installer who is NRTL listed or who is certified by LPI as a Master Installer/Designer.

#### Listing and Labeling:  As defined in NFPA 780, Article 2-2, “Definitions.”

#### Provide UL Master Label.

part 2 – products

## MANUFACTURERS

#### Available Manufacturer:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

##### A-C Lightning Security, Inc.

##### Automatic Lightning Protection.

##### Harger Lightning Protection, Inc.

##### Heary Bros. Lightning Protection Co. Inc.

##### Independent Protection Company, Inc.

##### Robbinson Lightning, Incorporated.

##### Thompson Lightning Protection, Inc.

## lightning protection system components

#### Comply with UL 96

#### Pole Mounted Air Terminals:  NFPA Class I, unless otherwise indicated.

#### Ground Rods, Ground Loop Conductors, and Concrete-Encased Electrodes:  Comply with Division 16 Section “Grounding and Bonding”

part 3 – execution

## installation\

#### Install lighting protection components and systems according to UL 96A and NFPA 780.

#### Install conductors with direct paths form air terminals to steel tower to ground connections.  Avoid sharp bends and narrow loops.

#### Cable Connections:  Use approved exothermic-welded connections for all conductor splices and connections between conductors and other components except those above single-ply membrane roofing.

#### A counterpoise installation based on requirements in Division 16 Section “Grounding and Bonding” may be used as a ground loop required by NFPA 780, provided counterpoise conductor meets or exceeds minimum requirements in NFPA 780.

##### Bond ground terminals to counterpoise conductor.

##### Bond grounded metal bodies on building within 12 feet (3.6m) of ground to counterpoise conductor.

## corrosion protection

#### Do not combine materials that can form an electrolytic couple that will accelerate corrosion in the presence of moisture unless moisture is permanently excluded from junction of such materials.

#### Use conductors with protective coatings where conditions would cause deterioration or corrosion of conductors.

## field quality control

#### UL Inspection:  Apply for inspection by UL as required to obtain a UL Master Label for system.

End of section 13100