SECTION 02821

CHAIN-LINK FENCES AND GATES

- GENERAL

      - RELATED DOCUMENTS

        - Drawings and general provisions of the Contract, including the General and Supplementary Conditions of the Contract and other Division 1 Specification Sections, apply to this Section.

      - SUMMARY

        - This Section includes the following:

          - Chain-Link Fences:  Industrial.

          - Gates:  Swing.

        - Related Section s include the following:

          - Division 2 Section "Earthwork" for site excavation, fill, and backfill where chain-link fences and gates are located.

          - Division 3 Section "Cast-in-Place Concrete" for concrete post fill.

      - SUBMITTALS

        - Product Data:  Include construction details, material descriptions, dimensions of individual components and profiles, and finishes for chain-link fences and gates.

          - Fence and gate posts, rails, and fittings.

          - Chain-link fabric, reinforcements, and attachments.

          - Gates and hardware.

        - Shop Drawings:  Show locations of fences, gates, posts, rails, tension wires, details of extended posts, extension arms, gate swing, or other operation, hardware, and accessories.  Indicate materials, dimensions, sizes, weights, and finishes of components.  Include plans, gate elevations, sections, details of post anchorage, attachment, bracing, and other required installation and operational clearances.

        - Qualification Data:  For Installer.

      - QUALITY ASSURANCE

        - Installer Qualifications:  An experienced installer who has completed chain-link fences and gates similar in material, design, and extent to those indicated for this Project and whose work has resulted in construction with a record of successful in-service performance.

      - PROJECT CONDITIONS

        - Field Measurements:  Verify layout information for chain-link fences and gates shown on Drawings in relation to property survey and existing structures.  Verify dimensions by field measurements.

        - Interruption of Existing Utility Service:  Do not interrupt utility services to facilities occupied by Owner or others unless permitted under the following conditions and then only after arranging to provide temporary utility services according to requirements indicated:

          - Notify Contracting Officer no fewer than five days in advance of proposed interruption of utility services.

          - Do not proceed with interruption of utility services without Contracting Officer's written permission.

- PRODUCTS

      - MANUFACTURERS

        - Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

          - Chain-Link Fences and Gates:

            - Ameristar Architectural Metal Fences and Gates.

            - Amico,   Alabama Metal Industries Corporation.

            - Anchor Fence Company

      - CHAIN-LINK FENCE FABRIC

        - General:  Height 6 ft.  Provide fabric in one-piece heights measured between top and bottom of outer edge of selvage knuckle or twist.  Comply with ASTM A 392, CLFMI CLF 2445, and requirements indicated below:

          - Steel Wire Fabric:  Metallic-coated wire with a diameter of 0.148 inch (3.76 mm).

            - Mesh Size:  2 inches (50 mm).

            - Weight of Metallic (Zinc) Coating:  ASTM A 392, Type II, Class 2, 2.0 oz./sq. ft. (610 g/sq. m) with zinc coating applied before weaving.

      - INDUSTRIAL FENCE FRAMING

        - Posts and Rails:  Comply with ASTM F 1043 for framing, ASTM F 1083 for Group IC round pipe, and the following:

          - Group:  IA, round steel pipe, Schedule 40.

          - Fence Height:  6 feet (1.83 m).

          - Strength Requirement:  Heavy industrial according to ASTM F 1043.

          - Post Diameter and Thickness:  According to ASTM F 1083.

            - Top Rail:  1.66 inches (42 mm).

            - Line Post:  2.375 inches (60 mm).

            - End, Corner and Pull Post:  2.875 inches (73 mm).

            - Swing Gate Post:  2.375-inch (60-mm) diameter, 3.11-lb/ft. (4.63-kg/m) weight.

          - Coating for Steel Framing:

            - Metallic Coating:

              - External, Type B, zinc with organic overcoat, consisting of a minimum of 0.9 oz./sq. ft. (0.27 kg/sq. m) of zinc after welding, a chromate conversion coating, and a clear, verifiable polymer film.  Internal, Type D, consisting of 81 percent, not less than 0.3-mil- (0.0076-mm-) thick, zinc pigmented coating.

              - Type C, Zn-5-Al-MM alloy, consisting of not less than 1.8-oz./sq. ft. (0.55-kg/sq. m) coating.

      - INDUSTRIAL SWING GATES

        - General:  Comply with ASTM F 900 for single swing gate types.

          - Metal Pipe and Tubing:  Galvanized steel.  Comply with ASTM F 1043 and ASTM F 1083 for materials and protective coatings.

        - Frames and Bracing:  Fabricate members from round, galvanized steel tubing with outside dimension and weight according to ASTM F 900 and the following:

          - Gate Fabric Height:  2 inches (50 mm) less than adjacent fence height.

          - Leaf Width:  As indicated on drawings.

          - Frame Members:

            - Tubular Steel:  1.90 inches (48 mm) round.

        - Frame Corner Construction:

          - Assembled with corner fittings and 5/16-inch- (7.9-mm-) diameter, adjustable truss rods for panels 5 feet (1.52 m) wide or wider.

        - Hardware:  Latches permitting operation from both sides of gate, hinges, and keepers for each gate leaf more than 5 feet (1.52 m) wide.  Fabricate latches with integral eye openings for padlocking; padlock accessible from both sides of gate.

      - FITTINGS

        - General:  Comply with ASTM F 626.

        - Post and Line Caps:  Provide for each post.

        - Rail and Brace Ends:  Attach rails securely to each gate, corner, pull, and end post.

        - Rail Fittings:  Provide the following:

          - Top Rail Sleeves:  Pressed-steel or round-steel tubing not less than 6 inches (152 mm) long.

          - Rail Clamps:  Line clamps for connecting intermediate or bottom rails in the fence line-to-line posts.

        - Tension and Brace Bands:  Pressed steel.

        - Tension Bars:  Steel, length not less than 2 inches (50 mm) shorter than full height of chain-link fabric.  Provide one bar for each gate and end post, and two for each corner and pull post, unless fabric is integrally woven into post.

        - Tie Wires, Clips, and Fasteners:  According to ASTM F 626.

          - Standard Round Wire Ties:  For attaching chain-link fabric to posts, rails, and frames, complying with the following:

            - Hot-Dip Galvanized Steel:  0.106-inch- (2.69-mm-) diameter wire; galvanized coating thickness matching coating thickness of chain-link fence fabric.

        - Finish:

          - Metallic Coating for Pressed Steel or Cast Iron:  Not less than 1.2 oz. /sq. ft. (366 g /sq. m) zinc.

      - CAST-IN-PLACE CONCRETE

        - Materials:  Portland cement complying with ASTM C 150, Type I aggregates complying with ASTM C 33, and potable water.

          - Concrete Mixes:  Normal-weight concrete with not less than 3000-psi (20.7- MPa) compressive strength (28 days), 3-inch (75-mm) slump, and 1-inch (25-mm) maximum size aggregate.

- EXECUTION

      - INSTALLATION

        - Install chain-link fencing to comply with ASTM F 567 and more stringent requirements specified.

        - Post Excavation:  Drill or hand-excavate holes for posts to diameters and spacings indicated, in firm, undisturbed soil.

        - Post Setting:  Set posts in concrete at indicated spacing into firm, undisturbed soil.

          - Verify that posts are set plumb, aligned, and at correct height and spacing, and hold in position during setting with concrete or mechanical devices.

          - Concrete Fill:  Place concrete around posts to dimensions indicated and vibrate or tamp for consolidation.  Protect aboveground portion of posts from concrete splatter.

            - Concealed Concrete:  Top 4 inches (50 mm) to allow covering with surface material.

        - Post Bracing and Intermediate Rails:  Install according to ASTM F 567, maintaining plumb position and alignment of fencing.  Install braces at end and gate posts and at both sides of corner and pull posts.

          - Locate horizontal braces at midheight of fabric 6 feet (1.83 m) or higher, on fences with top rail and at 2/3 fabric height on fences without top rail.  Install so posts are plumb when diagonal rod is under proper tension.

        - Top Rail:  Install according to ASTM F 567, maintaining plumb position and alignment of fencing.  Run rail continuously through line post caps, bending to radius for curved runs and terminating into rail end attached to posts or post caps fabricated to receive rail at terminal posts.  Provide expansion couplings as recommended in writing by fencing manufacturer.

        - Bottom Rails:  Install, spanning between posts.

        - Chain-Link Fabric:  Apply fabric to outside of enclosing framework.  Leave 2 inches (50 mm) between finish grade or surface and bottom selvage, unless otherwise indicated.  Pull fabric taut and tie to posts, rails, and tension wires.  Anchor to framework so fabric remains under tension after pulling force is released.

        - Tension or Stretcher Bars:  Thread through fabric and secure to end, corner, pull, and gate posts with tension bands spaced not more than 15 inches (380 mm) o.c.

        - Tie Wires:  Use wire of proper length to firmly secure fabric to line posts and rails.  Attach wire at 1 end to chain-link fabric, wrap wire around post a minimum of 180 degrees, and attach other end to chain-link fabric per ASTM F 626.  Bend ends of wire to minimize hazard to individuals and clothing.

          - Maximum Spacing:  Tie fabric to line posts at 12 inches (300 mm) o.c. and to braces at 24 inches (610 mm) o.c.

      - GATE INSTALLATION

        - Install gates according to manufacturer's written instructions, level, plumb, and secure for full opening without interference.  Attach fabric as for fencing.  Attach hardware using tamper-resistant or concealed means.  Install ground-set items in concrete for anchorage.  Adjust hardware for smooth operation and lubricate where necessary.

      - ADJUSTING

        - Gate:  Adjust gate to operate smoothly, easily, and quietly, free of binding, warp, excessive deflection, distortion, nonalignment, misplacement, disruption, or malfunction, throughout entire operational range.  Confirm that latches and locks engage accurately and securely without forcing or binding.

END OF SECTION 02821