SECTION 01500

- TEMPORARY FACILITIES AND CONTROLS

part 1 - GENERAL

## SUMMARY

#### This Section includes requirements for temporary facilities and controls, including temporary utilities, support facilities, and security and protection facilities.

#### See Division 1 Section "Execution Requirements" for progress cleaning requirements.

## DEFINITIONS

#### Permanent Enclosure:  As determined by Contracting Officer (CO), permanent or temporary roofing is complete, insulated, and weathertight; exterior walls are insulated and weathertight; and all openings are closed with permanent construction or substantial temporary closures.

## USE CHARGES

#### General:  Cost or use charges for temporary facilities are not chargeable to Government

#### Water Service:  Use water from Government’s existing water system without metering and without payment of use charges.

#### Electric Power Service:  Use electric power from Government existing system without metering and without payment of use charges.

## SUBMITTALS

#### Temporary Utility Reports:  Submit reports of tests, inspections, meter readings, and similar procedures performed on temporary utilities.

## QUALITY ASSURANCE

#### Standards:  Comply with ANSI A10.6, NECA's "Temporary Electrical Facilities," and NFPA 241.

##### Electric Service:  Comply with NECA, NEMA, and UL standards and regulations for temporary electric service.  Install service to comply with NFPA 70.

#### Tests and Inspections:  Arrange for authorities having jurisdiction to test and inspect each temporary utility before use.  Obtain required certifications and permits.

## PROJECT CONDITIONS

#### Temporary Utilities:  At earliest feasible time, when acceptable to Government, change over from use of temporary service to use of permanent service.

##### Temporary Use of Permanent Facilities:  Installer of each permanent service shall assume responsibility for operation, maintenance, and protection of each permanent service during its use as a construction facility before Government acceptance, regardless of previously assigned responsibilities.

#### Conditions of Use:  The following conditions apply to use of temporary services and facilities by all parties engaged in the Work:

##### Keep temporary services and facilities clean and neat.

##### Relocate temporary services and facilities as required by progress of the Work.

part 2 – PRODUCTS

## MATERIALS

#### General:  Provide new materials.  Undamaged, previously used materials in serviceable condition may be used if approved by CO.  Provide materials suitable for use intended.

#### Portable Chain-Link Fencing:  Minimum 2-inch (50-mm) 9-gage, galvanized steel, chain-link fabric fencing; minimum 6 feet (1.8 m) high with galvanized steel pipe posts; minimum 2-3/8-inch- (60-mm-) OD line posts and 2-7/8-inch- (73-mm-) OD corner and pull posts, with 1-5/8-inch- (42-mm-) OD top and bottom rails.  Provide galvanized steel bases for supporting posts.

#### Water:  Potable.

## EQUIPMENT

#### Field Offices:  Prefabricated, mobile units, or job-built construction with lockable entrances, operable windows, and serviceable finishes; heated and air conditioned; on foundations adequate for normal loading.

#### Fire Extinguishers:  Hand carried, portable, UL rated.  Provide class and extinguishing agent as indicated or a combination of extinguishers of NFPA-recommended classes for exposures.

##### Comply with NFPA 10 and NFPA 241 for classification, extinguishing agent, and size required by location and class of fire exposure.

#### Self-Contained Toilet Units:  Single-occupant units of chemical, aerated recirculation, or combustion type; vented; fully enclosed with a glass-fiber-reinforced polyester shell or similar nonabsorbent material.

#### Drinking-Water Fixtures:  Containerized, tap-dispenser, bottled-water, drinking-water units, including paper cup supply.

#### Heating Equipment:  Unless CO authorizes use of permanent heating system, provide vented, self-contained, liquid-propane-gas or fuel-oil heaters with individual space thermostatic control.

##### Use of gasoline-burning space heaters, open-flame heaters, or salamander-type heating units is prohibited.

##### Heating Units:  Listed and labeled, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use for type of fuel being consumed.

#### Electrical Outlets:  Properly configured, NEMA-polarized outlets to prevent insertion of 110- to 120-V plugs into higher-voltage outlets; equipped with ground-fault circuit interrupters, reset button, and pilot light.

#### Power Distribution System Circuits:  Where permitted and overhead and exposed for surveillance, wiring circuits, not exceeding 125-V ac, 20-A rating, and lighting circuits may be nonmetallic sheathed cable.

PART 3 – EXECUTION

## INSTALLATION, GENERAL

#### Locate facilities where they will serve Project adequately and result in minimum interference with performance of the Work.  Relocate and modify facilities as required.

#### Provide each facility ready for use when needed to avoid delay.  Maintain and modify as required.  Do not remove until facilities are no longer needed or are replaced by authorized use of completed permanent facilities.

## TEMPORARY UTILITY INSTALLATION

#### General:  Engage appropriate local utility company to install temporary service or connect to existing service.  Where utility company provides only part of the service, provide the remainder with matching, compatible materials and equipment.  Comply with utility company recommendations.

##### Arrange with utility company, CO, and existing users for time when service can be interrupted, if necessary, to make connections for temporary services.

##### Provide adequate capacity at each stage of construction.  Before temporary utility is available, provide trucked-in services.

##### Obtain easements to bring temporary utilities to Project site where Government easements cannot be used for that purpose.

#### Sewers and Drainage:  If sewers are available, provide temporary connections to remove effluent that can be discharged lawfully.  If sewers are not available or cannot be used, provide drainage ditches, dry wells, stabilization ponds, and similar facilities.  If neither sewers nor drainage facilities can be lawfully used for discharge of effluent, provide containers to remove and dispose of effluent off-site in a lawful manner.

##### Filter out excessive soil, construction debris, chemicals, oils, and similar contaminants that might clog sewers or pollute waterways before discharge.

##### Maintain temporary sewers and drainage facilities in a clean, sanitary condition.  After heavy use, restore normal conditions promptly.

##### Provide temporary filter beds, settlement tanks, separators, and similar devices to purify effluent to levels acceptable to authorities having jurisdiction.

#### Water Service:  Install water service and distribution piping in sizes and pressures adequate for construction until permanent water service is in use.  Sterilize temporary water piping before use.

#### Water Service:  Use of Government existing water service facilities will be permitted, as long as facilities are cleaned and maintained in a condition acceptable to CO.  At Substantial Completion, restore these facilities to condition existing before initial use.

##### Provide rubber hoses as necessary to serve Project site.

#### Sanitary Facilities:  Provide temporary toilets, wash facilities, and drinking-water fixtures.  Comply with regulations and health codes for type, number, location, operation, and maintenance of fixtures and facilities.

##### Disposable Supplies:  Provide toilet tissue, paper towels, paper cups, and similar disposable materials for each facility.  Maintain adequate supply.  Provide covered waste containers for disposal of used material.

##### Toilets:  Use of Government existing toilet facilities will be permitted, as long as facilities are cleaned and maintained in a condition acceptable to CO.  At Substantial Completion, restore these facilities to condition existing before initial use.

##### Toilets:  Install self-contained toilet units.  Shield toilets to ensure privacy.

#### Heating and Cooling:  Provide temporary heating and cooling required by construction activities for curing or drying of completed installations or for protecting installed construction from adverse effects of low temperatures or high humidity.  Select equipment from that specified that will not have a harmful effect on completed installations or elements being installed.

##### Maintain a minimum temperature of 50 deg F (10 deg C) in permanently enclosed portions of building for normal construction activities, and 65 deg F (18.3 deg C) for finishing activities and areas where finished Work has been installed.

#### Ventilation and Humidity Control:  Provide temporary ventilation required by construction activities for curing or drying of completed installations or for protecting installed construction from adverse effects of high humidity.  Select equipment from that specified that will not have a harmful effect on completed installations or elements being installed.  Coordinate ventilation requirements to produce ambient condition required and minimize energy consumption.

#### Electric Power Service:  Provide weatherproof, grounded electric power service and distribution system of sufficient size, capacity, and power characteristics during construction period.  Include meters, transformers, overload-protected disconnecting means, automatic ground-fault interrupters, and main distribution switchgear.

##### Install electric power service underground, unless overhead service must be used.

##### Install power distribution wiring overhead and rise vertically where least exposed to damage.

#### Electric Power Service:  Use of Government's existing electric power service will be permitted, as long as equipment is maintained in a condition acceptable to CO.

#### Electric Distribution:  Provide receptacle outlets adequate for connection of power tools and equipment.

##### Provide waterproof connectors to connect separate lengths of electrical power cords if single lengths will not reach areas where construction activities are in progress.  Do not exceed safe length-voltage ratio.

#### Lighting:  Provide temporary lighting with local switching that provides adequate illumination for construction operations and traffic conditions.

##### Install and operate temporary lighting that fulfills security and protection requirements without operating entire system.

#### Telephone Service:  Provide temporary telephone service throughout construction period for common-use facilities used by all personnel engaged in construction activities.

##### Provide a portable cellular telephone for superintendent's use in making and receiving telephone calls when away from field office.

## SUPPORT FACILITIES INSTALLATION

#### General:  Comply with the following:

##### Locate field offices, storage sheds, sanitary facilities, and other temporary construction and support facilities for easy access.

##### Maintain support facilities until near Substantial Completion.  Remove before Substantial Completion.  Personnel remaining after Substantial Completion will be permitted to use permanent facilities, under conditions acceptable to CO.

#### Temporary Roads and Paved Areas:  Construct and maintain temporary roads and paved areas adequate to support loads and to withstand exposure to traffic during construction period.  Locate temporary roads and paved areas as indicated on Drawings.

#### Temporary Roads and Paved Areas:  Construct and maintain temporary roads and paved areas adequate to support loads and to withstand exposure to traffic during construction period.  Locate temporary roads and paved areas in same location as permanent roads and paved areas.  Extend temporary roads and paved areas, within construction limits indicated, as necessary for construction operations.

##### Coordinate elevations of temporary roads and paved areas with permanent roads and paved areas.

##### Prepare subgrade and install subbase and base for temporary roads and paved areas according to Division 2 Section "Earthwork."

#### Dewatering Facilities and Drains:  Comply with requirements in applicable Division 2 Sections for temporary drainage and dewatering facilities and operations not directly associated with construction activities included in individual Sections.  Where feasible, use same facilities.  Maintain Project site, excavations, and construction free of water.

#### Project Identification and Temporary Signs:  Prepare Project identification and other signs in sizes indicated.  Install signs where indicated to inform public and persons seeking entrance to Project.  Do not permit installation of unauthorized signs.

##### Engage an experienced sign painter to apply graphics for Project identification signs.  Comply with details indicated.

##### Prepare temporary signs to provide directional information to construction personnel and visitors.

#### Waste Disposal Facilities:  Provide waste-collection containers in sizes adequate to handle waste from construction operations.  Containerize and clearly label hazardous, dangerous, or unsanitary waste materials separately from other waste.  Comply with Division 1 Section "Execution Requirements " for progress cleaning requirements.

##### If required by authorities having jurisdiction, provide separate containers, clearly labeled, for each type of waste material to be deposited.

#### Storage and Fabrication Sheds:  Provide sheds sized, furnished, and equipped to accommodate materials and equipment involved, including temporary utility services.  Sheds may be open shelters or fully enclosed spaces within building or elsewhere on-site.

## SECURITY AND PROTECTION FACILITIES INSTALLATION

#### Environmental Protection:  Provide protection, operate temporary facilities, and conduct construction in ways and by methods that comply with environmental regulations and that minimize possible air, waterway, and subsoil contamination or pollution or other undesirable effects.  Avoid using tools and equipment that produce harmful noise.  Restrict use of noisemaking tools and equipment to hours that will minimize complaints from persons or firms near Project site.

#### Stormwater Control:  Provide earthen embankments and similar barriers in and around excavations and subgrade construction, sufficient to prevent flooding by runoff of stormwater from heavy rains.

#### Tree and Plant Protection:  Install temporary fencing located as indicated or outside the drip line of trees to protect vegetation from construction damage.  Protect tree root systems from damage, flooding, and erosion.

#### Site Enclosure Fence: When excavation begins, install enclosure fence with lockable entrance gates.  Locate where indicated, or enclose entire Project site or portion determined sufficient to accommodate construction operations.  Install in a manner that will prevent people, dogs, and other animals from easily entering site except by entrance gates.

##### Set portable chain-link fence posts in concrete bases.

##### Provide gates in sizes and at locations necessary to accommodate delivery vehicles and other construction operations.

#### Security Enclosure and Lockup:  Install substantial temporary enclosure around partially completed areas of construction.  Provide lockable entrances to prevent unauthorized entrance, vandalism, theft, and similar violations of security.

#### Barricades, Warning Signs, and Lights:  Comply with standards and code requirements for erecting structurally adequate barricades.  Paint with appropriate colors, graphics, and warning signs to inform personnel and public of possible hazard.  Where appropriate and needed, provide lighting, including flashing red or amber lights.

#### Temporary Enclosures:  Provide temporary enclosures for protection of construction, in progress and completed, from exposure, foul weather, other construction operations, and similar activities.  Provide temporary weathertight enclosure for building exterior.

##### Where heating or cooling is needed and permanent enclosure is not complete, provide insulated temporary enclosures.  Coordinate enclosure with ventilating and material drying or curing requirements to avoid dangerous conditions and effects.

##### Vertical Openings:  Close openings of 25 sq. ft. (2.3 sq. m) or less with plywood or similar materials.

##### Horizontal Openings:  Close openings in floor or roof decks and horizontal surfaces with load-bearing, wood-framed construction.

##### Install tarpaulins securely using fire-retardant-treated wood framing and other materials.

#### Temporary Partitions:  Erect and maintain dustproof partitions and temporary enclosures to limit dust and dirt migration and to separate areas from fumes and noise.

##### Construct dustproof partitions of not less than nominal 4-inch (100-mm) studs, 5/8-inch (16-mm) gypsum wallboard with joints taped on occupied side, and 1/2-inch (13-mm) fire-retardant plywood on construction side.

#### Temporary Fire Protection:  Until fire-protection needs are supplied by permanent facilities, install and maintain temporary fire-protection facilities of types needed to protect against reasonably predictable and controllable fire losses.  Comply with NFPA 241.

##### Provide fire extinguishers, installed on walls on mounting brackets, visible and accessible from space being served, with sign mounted above.

###### Locate fire extinguishers where convenient and effective for their intended purpose; provide not less than one extinguisher on each floor at or near each usable stairwell.

##### Store combustible materials in containers in fire-safe locations.

##### Maintain unobstructed access to fire extinguishers, fire hydrants, temporary fire-protection facilities, stairways, and other access routes for firefighting.  Prohibit smoking in hazardous fire-exposure areas.

##### Supervise welding operations, combustion-type temporary heating units, and similar sources of fire ignition.

##### Permanent Fire Protection:  At earliest feasible date in each area of Project, complete installation of permanent fire-protection facility, including connected services, and place into operation and use.  Instruct key personnel on use of facilities.

##### Develop and supervise an overall fire-prevention and first-aid fire-protection program for personnel at Project site.  Review needs with local fire department and establish procedures to be followed.  Instruct personnel in methods and procedures.  Post warnings and information.

##### Provide hoses for fire protection of sufficient length to reach construction areas.  Hang hoses with a warning sign stating that hoses are for fire-protection purposes only and are not to be removed.  Match hose size with outlet size and equip with suitable nozzles.

## OPERATION, TERMINATION, AND REMOVAL

#### Supervision:  Enforce strict discipline in use of temporary facilities.  To minimize waste and abuse, limit availability of temporary facilities to essential and intended uses.

#### Maintenance:  Maintain facilities in good operating condition until removal.  Protect from damage caused by freezing temperatures and similar elements.

##### Maintain operation of temporary enclosures, heating, cooling, humidity control, ventilation, and similar facilities on a 24-hour basis where required to achieve indicated results and to avoid possibility of damage.

##### Prevent water-filled piping from freezing.  Maintain markers for underground lines.  Protect from damage during excavation operations.

#### Termination and Removal:  Remove each temporary facility when need for its service has ended, when it has been replaced by authorized use of a permanent facility, or no later than Substantial Completion.  Complete or, if necessary, restore permanent construction that may have been delayed because of interference with temporary facility.  Repair damaged Work, clean exposed surfaces, and replace construction that cannot be satisfactorily repaired.

##### Materials and facilities that constitute temporary facilities are the property of Contractor.  Owner reserves right to take possession of Project identification signs.

##### At Substantial Completion, clean and renovate permanent facilities used during construction period.  Comply with final cleaning requirements in Division 1 Section "Closeout Procedures."

END OF SECTION 01500