# SECTION 02300

# EARTHWORK

- GENERAL

      - RELATED DOCUMENTS

        - Drawings and general provisions of the Contract and other Division 1 Specifications Sections, apply to this Section.

      - SUMMARY

        - This Section includes the following:

          - Preparing subgrades for slabs-on-grade.

          - Excavating, backfilling and compacting of backfill material for footings and trenches.

        - Related Sections include the following:

          - Division 1 Section "Construction Facilities and Temporary Controls."

          - Division 1 Section “Quality Requirements”

      - DEFINITIONS

        - Backfill:  Soil materials used to fill an excavation.

        - Borrow:  Satisfactory soil imported from off-site for use as fill or backfill.

        - Excavation:  Removal of material encountered above subgrade elevations.

          - Additional Excavation:  Excavation below subgrade elevations as directed by Contracting Officer.  Additional excavation and replacement material will be paid for according to Contract provisions for changes in the Work.

          - Unauthorized Excavation:  Excavation below subgrade elevations or beyond indicated dimensions without direction by Contracting Officer.  Unauthorized excavation, as well as remedial work directed by Contracting Officer, shall be without additional compensation.

        - Fill:  Soil materials used to raise existing grades.

        - Rock:  Rock material in beds, ledges, unstratified masses, and conglomerate deposits and boulders of rock material 3/4 cu. yd. or more in volume that when tested by an independent geotechnical testing agency, according to ASTM D 1586, exceeds a standard penetration resistance of 100 blows/2 inches.

        - Structures:  Footings, foundations or other man-made stationary features constructed above or below the ground surface.

        - Subgrade:  Surface or elevation remaining after completing excavation, or top surface of a fill or backfill immediately below base course, drainage fill, or topsoil materials.

        - Utilities include on-site underground pipes, conduits, ducts, and cables, as well as underground services.

      - SUBMITTALS

        - Material Test Reports:  From a qualified testing agency indicating and interpreting test results for compliance of the following with requirements indicated:

          - Classification according to ASTM D 2487 of each on-site or borrow soil material proposed for fill and backfill.

          - Laboratory compaction curve according to ASTM D 698 for each on-site or borrow soil material proposed for fill and backfill.

      - QUALITY ASSURANCE

        - Geotechnical Testing Agency Qualifications:  An independent testing agency qualified according to ASTM E 329 to conduct soil materials and rock-definition testing, as documented according to ASTM D 3740 and ASTM E 548.

      - PROJECT CONDITIONS

        - Project Site information. A Geotechnical report has been prepared for this project and is available upon request.

        - Existing Utilities:  Do not interrupt utilities serving facilities occupied by Government or others unless permitted in writing by Contracting Officer and then only after arranging to provide temporary utility services according to requirements indicated:

          - Notify Contracting Officer not less than five days in advance of proposed utility interruptions.

          - Do not proceed with utility interruptions without Contracting Officer's written permission.

          - Contact utility-locator service for area where Project is located before excavating.

- PRODUCTS

      - SOIL MATERIALS

        - General:  Provide satisfactory borrow soil materials.

1.	Satisfactory Soils:  Granular structural fill as specified in the Montana Public Works Standard Specifications (MPWSS).  See geotechnical report for additional information.

B.	Select Structural Fill Materials, Backfill and Fill

1.	Satisfactory soil materials shall meet the following general requirements for 6” minus sub-base course:

Screen or Sieve Size	Percent Passing By Weight

6.0 inches	100

No. 4	25-60

No. 200	2-10

Maximum Plasticity Index = 6

2.	Satisfactory soil materials shall meet the following general requirements for ¾ minus crushed base course:

Screen or Sieve Size	Percent Passing By Weight

¾” inches	100

No. 4	40-70

No. 10	25-55

No. 200	2-10

Maximum Plasticity Index = 6

C.	Lean Concrete

1.	A flowable fill comprised of low strength concrete with a minimum of 1/2 sack of cement per cubic yard.

- EXECUTION

      - PREPARATION

        - Protect structures, utilities, sidewalks, pavements, and other facilities from damage caused by settlement, lateral movement, undermining, washout, and other hazards created by earthwork operations.

        - Protect subgrades and foundation soils against freezing temperatures or frost and moisture.    Provide protective insulating materials, water diversion measures, excavation covers and water removal as necessary.  See geotechnical report for additional information.

        - Provide erosion-control measures to prevent erosion or displacement of soils and discharge of soil-bearing water runoff or airborne dust to adjacent properties and walkways.

      - DEWATERING

        - Prevent surface water and ground water from entering excavations, from ponding on prepared subgrades, and from flooding Project site and surrounding area.

        - Protect subgrades from softening, undermining, washout, and damage by rain or water accumulation.

          - Reroute surface water runoff away from excavated areas.  Do not allow water to accumulate in excavations.  Do not use excavated trenches as temporary drainage ditches.

          - Install a dewatering system to keep subgrades dry and convey ground water away from excavations.  Maintain until dewatering is no longer required.

      - EXPLOSIVES

        - Explosives:  Do not use explosives.

      - EXCAVATION, GENERAL

        - Unclassified Excavation:  Excavation to subgrade elevations regardless of the character of surface and subsurface conditions encountered, including rock, soil materials, and obstructions.

          - If excavated materials intended for fill and backfill include unsatisfactory soil materials and rock, replace with satisfactory soil materials.

      - EXCAVATION FOR STRUCTURES

        - Excavate to indicated elevations and dimensions within a tolerance of plus or minus 1 inch.  Extend excavations a sufficient distance from structures for placing and removing concrete formwork, for installing services and other construction, and for inspections.

          - Excavations for Footings and Foundations:  Do not disturb bottom of excavation.  Excavate by hand to final grade just before placing concrete reinforcement.  Trim bottoms to required lines and grades to leave solid base to receive other work.

      - APPROVAL OF SUBGRADE

        - Notify Contracting Officer when excavations have reached required subgrade.

        - If Contracting Officer determines that unsatisfactory soil is present, continue excavation and replace with compacted backfill or fill material as directed.

          - Additional excavation and replacement material will be paid for according to Contract provisions.

        - Proof roll subgrade with heavy pneumatic-tired equipment to identify soft pockets and areas of excess yielding.  Do not proof roll wet or saturated subgrades.

        - Reconstruct subgrades damaged by freezing temperatures, frost, rain, accumulated water, or construction activities, as directed by Contracting Officer.

      - UNAUTHORIZED EXCAVATION

        - Fill unauthorized excavation under foundations by extending bottom elevation of concrete foundation or footing to excavation bottom, without altering top elevation.  Lean concrete fill may be used when approved by Contracting Officer.

          - Fill unauthorized excavations under other construction as directed by Contracting Officer at no expense to the Government.

      - STORAGE OF SOIL MATERIALS

        - Stockpile borrow materials and satisfactory excavated soil materials.  Stockpile soil materials without intermixing.  Place, grade, and shape stockpiles to drain surface water.  Cover to prevent windblown dust.

          - Stockpile soil materials away from edge of excavations.  Do not store within drip line of remaining trees.

      - BACKFILL

        - Place and compact backfill in excavations promptly, but not before completing the following:

          - Construction below finish grade including, where applicable, dampproofing, waterproofing, and placement of geotextiles.

          - Removing concrete formwork.

          - Removing trash and debris.

          - Removing temporary shoring and bracing, and sheeting.

      - FILL

        - Preparation:  Remove vegetation, topsoil, debris, unsatisfactory soil materials, obstructions, and deleterious materials from ground surface before placing fills.

        - Plow, scarify, bench, or break up sloped surfaces steeper than 1 vertical to 4 horizontal so fill material will bond with existing material.

        - Place and compact fill material in layers to required elevations as follows:

          - Under grass and planted areas, use satisfactory soil material.

          - Under walks and pavements, use leveling/cushion course on acceptable structural fill.

          - Under footings and foundations, structural fill.

      - MOISTURE CONTROL

        - Uniformly moisten or aerate subgrade and each subsequent fill or backfill layer before compaction to within 2 percent of optimum moisture content.

          - Do not place backfill or fill material on surfaces that are muddy, frozen, or contain frost or ice.

          - Remove and replace, or scarify and air-dry, otherwise satisfactory soil material that exceeds optimum moisture content by 2 percent and is too wet to compact to specified dry unit weight.

      - COMPACTION OF BACKFILLS AND FILLS

        - Place backfill and fill materials in layers not more than 1.5 times the nominal aggregate size.  See geotechnical report for additional information.

        - Place backfill and fill materials evenly on all sides of structures to required elevations, and uniformly along the full length of each structure.

        - Compact structural fill and backfill to not less than 95% of maximum dry density according to ASTM D 698.  See geotechnical report for additional information.

      - GRADING

        - General:  Uniformly grade areas to a smooth surface, free from irregular surface changes.  Comply with compaction requirements and grade to cross sections, lines, and elevations indicated.

          - Provide a smooth transition between adjacent existing grades and new grades.

          - Cut out soft spots, fill low spots, and trim high spots to comply with required surface tolerances.

        - Site Grading:  Slope grades to direct water away from structures and to prevent ponding.  Finish subgrades to required elevations within the following tolerances:

          - Lawn or Unpaved Areas:  Plus or minus 1 inch.

          - Walks:  Plus or minus 1 inch.

        - Grading inside Structure Lines:  Finish subgrade to a tolerance of 1/2 inch when tested with a 10-foot straightedge.

      - FIELD QUALITY CONTROL

        - Testing Agency:  Contractor shall engage a qualified independent geotechnical engineering testing agency to perform field quality-control testing.

        - Allow testing agency to inspect and test subgrades and each fill or backfill layer.  Proceed with subsequent earthwork only after test results for previously completed work comply with requirements.

        - Footing Subgrade:  At footing subgrades, at least one test of each soil stratum will be performed to verify design bearing capacities.  Subsequent verification and approval of other footing subgrades may be based on a visual comparison of subgrade with tested subgrade when approved by Contracting Officer.

        - Testing agency will test compaction of soils in place according to ASTM D 1556, ASTM D 2167, ASTM D 2922, and ASTM D 2937, as applicable.  Tests will be performed at the following locations and frequencies:

          - Foundation Structural Fill:  No fewer than three tests at each Structural Fill layer.

          - Backfill:  No fewer than two tests at each compacted Backfill layer.

        - When testing agency reports that subgrades, fills, or backfills have not achieved degree of compaction specified, scarify and moisten or aerate, or remove and replace soil to depth required; recompact and retest until specified compaction is obtained.

      - PROTECTION

        - Protecting Graded Areas:  Protect newly graded areas from moisture, traffic, freezing, and erosion.  Keep free of trash and debris.

        - Repair and reestablish grades to specified tolerances where completed or partially completed surfaces become eroded, rutted, settled, or where they lose compaction due to subsequent construction operations or weather conditions.

          - Scarify or remove and replace soil material to depth as directed by Contracting Officer; reshape and recompact.

        - Where settling occurs before Project correction period elapses, remove finished surfacing, backfill with additional soil material, compact, and reconstruct surfacing.

          - Restore appearance, quality, and condition of finished surfacing to match adjacent work, and eliminate evidence of restoration to the greatest extent possible.

      - DISPOSAL OF SURPLUS AND WASTE MATERIALS

        - Disposal:  Remove surplus satisfactory soil and waste material, including unsatisfactory soil, trash, and debris, and legally dispose of it off Government property.

- END OF SECTION 02300