RAPPEL TOWER

ANNUAL PRE-USE CONDITION ASSESSMENT

CHECKLIST FORM

(To be completed by the Base Manager)

| Tower Name | Missoula AFD Rappel Tower |
| --- | --- |
| Date of Inspection |  |
| Inspected By |  |

|  | Yes | No | Remarks |
| --- | --- | --- | --- |
| Tower and Simulator - Overall Condition |  |  |  |
| Is the tower or simulator leaning or twisted? |  |  | If the tower or simulator is leaning or twisted, it should not be used and engineering should be contacted immediately. |
| Are there any broken or hanging members? |  |  | Any broken or hanging member will be required to be fixed before the tower can be used. Fixing major members may require a special inspection by the Regional Bridge Engineer or a qualified representative. |
| Are there any obvious missing parts? |  |  | Any missing parts will have to be replaced before the tower can be used. |
| Are all “X” bracing rods straight? |  |  | If any rod is bent or curved, this is an indication of a problem and the tower should not be used until the reason for the bent rod is found and corrected. |
| Is the lightning protection system intact and functional? |  |  | Lightning protection system must be functional before the tower can be used. |
| Is the aircraft warning light system working? |  |  | The warning light system must function at all times and the tower may be not used when they are not functional. |
| Tower |  |  |  |
| Are all faying surfaces at all connections in firm contact? |  |  | If faying surfaces are not in firm contact, this may be an indication of movement of the tower or twisting or bending of a beam. |
| Are all grating properly installed with adequate attachment to supporting framework? |  |  | Any lose grating must be secured to the supporting framework before the tower can be used. |
| Are all anchor rods and bolts snug and tightened to 200 ft-lbs torque? |  |  | If any rod is bent or curved, this is an indication of a problem and the tower should not be used until the reason for the bent rod is found and corrected. |
| Is at least one full thread for all bolts and anchor rods projected beyond the face of the nut? |  |  | If at least one full thread does not project beyond the face of the nut, this could be an indication of a problem and the tower should not be used until the reason is found and corrected. |
| Are “X” bracing rods installed under tension with no detectable sag? |  |  | If any rod is bent or curved, this is an indication of a problem and the tower should not be used until the reason for the bent rod is found and corrected. |
| Is the tower plumb and free from twisting or racking? |  |  | If the tower or simulator is leaning or twisted, it should not be used and engineering should be contacted immediately. |
| Are all members in good repair, checked for missing, cracked or broken parts? |  |  | Any broken or hanging member will be required to be fixed before the tower can be used. Fixing major members may require a special inspection by the Regional Bridge Engineer or a qualified representative. |
| Do all gates have properly working closing mechanisms and latches? |  |  | All gates must work and provide protect from entering areas where falling can occur before the tower can be used. |
| Are all handrails present to provide fall protection? |  |  | Any missing parts will have to be replaced before the tower can be used. |
| Have all the anchor points for rappellers and spotters been removed and NDT’d or replaced and been installed per manufacturer’s recommendations? |  |  | This can be done by tapping on the bolts with a carabineer and if they are loose, they will rattle or checked with a torque wrench. |
| Has all damaged paint been repaired? |  |  | Damaged paint should be repaired as soon as possible to help increase longevity of the tower. |

| Simulator |  |  |  |
| --- | --- | --- | --- |
| Are all faying surfaces at all connections in firm contact? |  |  | If faying surfaces are not in firm contact, this may be an indication of movement of the simulator or twisting or bending of a beam. |
| Are all grating properly fastened to supporting framework? |  |  | Any lose grating must be secured to the supporting framework before the tower can be used. |
| Are all members square, true and plum? |  |  | If members are not square and plum for the simulator, it should not be used and engineering should be contacted immediately. |
| Do all gates and doors work properly and have properly working closing mechanisms and latches? |  |  | The doors must slide easily, latch and provide safety when closed. |
| Have all weep holes been cleaned out? |  |  | Weep holes need to be open to allow any moisture that gets into the HSS to drip out. |
| Have all the anchor points for rappellers and spotters been removed and NDT’d or replaced and installed per manufacturer’s recommendations? |  |  | This can be done by tapping on the bolts with a carabineer and if they are loose, they will rattle or checked with a torque wrench. |
| Have all long and short plates, skid and J step been inspected? Include non-destructive testing method to identify cracks (minimum to be liquid dye penetration testing), check for bend, twist and racking. |  |  | All plates must be checked each year before the tower can be used. |
| Has all damaged paint been repaired? |  |  | Damaged paint should be repaired as soon as possible to help increase longevity of the simulator. |

If any of the questions have been answered with a “No”, the problem must be fixed before any training is allowed on the tower.